  - 6-01-140 – Attachment of Communication Company Facilities on PPL Company Poles

    - 6-01-140-B, BA and D - Clarified the clearance from a communication cable to a streetlight drip loop.

    - 6-01-140-A and B – Added primary underground cable to the 30” exception in the Note.

    - 6-01-140-C – Changed wording from Communication Messenger-Mounted Cabinet to Communication Messenger-Mounted Passive Equipment to prevent confusion.

    - Note 1 – Added reference to 6-01-160 for wireless antennas.

    - Note 5 – Added spacing for drilled holes in wood poles.  Added language to clarify exceptions for drilling a metal pole.

    - Note 6 – Added “written” approval.

    - New Note 7 – Definition of a Communication Service Drop.

    - Renumbered notes 7 – 42 accordingly to 8 – 43.  Changed note numbers is drawings to match.

    - Note 9 (old 8) – Changed the in-span clearance from neutral, multiplex secondary or aerial cable to a communication cable with a bonded messenger to 12 inches per NESC 2017 Rule 235C2b1b exception 1.

    - Note 11j (old 10j) – Added a note about double container cars.

    - Note 16 (old 15) – Moved note about back bolting from note 17 into 16.  Added approved “in writing”.

    - Note 17 (old 16) – Added clarification to limit the use of bolt extenders.

    - Note 27 (old 26) – Clarified language on what a cabinet is and removed the term “equipment cases”. Added that approval for exceptions must be granted by PPL in writing.

    - Notes 28 and 29 (old 27 and 28) – removed the word “equipment case” to prevent confusion.

    - Note 36 (old 35) – Added approved “in writing”.

    - Note 38 (old 37) – Added “written” approval.